## 1 BGNM Program Overview
Build Green NM Certification Program Overview
Version 2015.05 (Dec 2015)
Version Information | [10 empty] | B9Nm2015.05
This is the 3rd major revision to the Build Green NM Certification Program. In 2003 we based our program on the NAHB Model Green Home Building Guidelines. In 2009 and 2013 we adopted and modified the editions of the ANSI approved National Green Building Standard ICC-700 (2008 and 2012 versions respectively).
This 2014 version is based on the 2012 and 2015 IECC, ASHRAE 62.2 and the 2012 NGBS ICC-700 and extensively modified for the southwest. For further questions and comments contact Steve Hale; Program Director at BGNM@Comcast.net or 505-688-5335.
Introduction
This program revision raises the bar for energy and water efficiency. It also is more user friendly and easier to show the client all the benefits of building a tight, efficient and comfortable home. The Certificate of Certification relays an easy and powerful message to the buying public that will separate your certified home from the others that merely build to code.
WEiR (Water Efficiency indoor Rating) Index
The WEiR Index is a new indoor water use index designed specifically by and for Build Green NM. The WEiR index score shows the efficiency of indoor water use in a single number. It works like the HERS Index in that it compares industry standard water use rates with installed fixtures and appliances. All industry standard appliances and fixtures would have a WEiR Index of 100. The maximum allowed WEiR Index is based on using all WaterSense fixtures, hot water waste of 0.75 gallons and an Energy Star dishwasher. The Build Green NM required WEiR Index is 75 or lower for certification. If a circulation system is installed for reducing hot water waste it is best if it is a demand controlled pump. WaterSense sets the bar for flow rates, however all fixtures are not required to be WaterSense labeled as long as they meet the average WaterSense flow rates overall throughout the home.
Certification Levels
There are four levels of certification in the Build Green NM certification program. The levels get more stringent as they go from Bronze to Emerald but be assured that even the Bronze Level of Certification is for homes that are built beyond code and will perform well for the home owner. The certification process requires satisfying certain mandatory practices and achieving a minimum level of points for optional practices. The optional practices receive points and the level of the home is determined by the number of points attained in energy and water efficiency and then overall additional points along with completion of the mandatory practices.
Certification Level Descriptions
Bronze Level | The Bronze Level of certification requires completion of all of the Mandatory Practices. There are no requirements for additional points which make this a Prescriptive Path to certification. A HERS Index of 70 and a WEiR Index of 75 are the maximum indexes allowed for energy and water efficiency.
Silver Level | The Silver level of certification requires completion of all Mandatory Practices. A HERS of 60 (before solar) and additional points for water efficiency and other categories. This HERS Index Baseline of 60 shall not include PV.
Gold Level | For the Gold and Emerald levels of certification, the HERS Index is determined by the Climate Zone that the project is constructed in and ranges from a HERS 51 in the south of NM to a HERS 54 in the Albuquerque metro are, and a HERS 55 in Santa Fe. PV may be used to further lower the HERS Index. For water efficiency you must earn additional points in addition to meeting or beating the required WEiR Index. Plus additional points from any category.
Emerald Level | Think of this level as a "Show or Demonstration Home". The HERS Index must be 20% lower than the Gold threshold. Water Efficiency must be higher than the Gold level and ERV / HRV Ventilation is Required. Plus additional Points from any category. Recommended; (1) A water catchment system for rain or grey water should have at least 500 gallons of capacity. (2) 50% of remaining roof area shall be directed to planting swales or storage. (3) The landscape Plan shall be complete in detail to show any area not yet installed (garden area for example). (4) Outdoor landscape is not required to be entirely completed but all turf must be in and at 10% or less of landscape area. The "front" landscape should be complete with all low flow (drip) irrigation be in place.
Certification Requirements by Certification Level and Efficiency Categories
|  | Energy |  |  | Water | IAQ |  | Sustainability | Additional Points from ANY Category | Total Points from ALL Categories
Mandatory Requirements - ALL Certification Levels |  | Mandatory Practices Required |  |  | Mandatory Practices Required | Mandatory Practices Required |  | Mandatory Practices Required
Bronze Level |  | HERS Index <= 70 any CZ |  |  | WEiR Index <= 75 | Mandatory Practices Required |  | Mandatory Practices Required | 0 | 0
Silver Level |  | HERS Index <= 60 any CZ |  |  | WEiR Index <=75, and 31 total points from Water Efficiency practices | Mandatory Practices Required |  | Mandatory Practices Required | 9 | 40
Gold Level |  |  | CZ 3 | 51 | WEiR Index <= 75, and 40 total points from Water Efficiency practices | Mandatory Practices Required, Plus 5 Points |  | Mandatory Practices Required, Plus 5 Points | 20 | 70
|  |  | CZ 4 | 54
|  |  | CZ 5 | 55
|  |  | CZ 6 | 54
|  |  | CZ 7 | 53
Emerald Level |  |  | CZ 3 | 41 | WEiR Index <= 75, and 48 total points from Water Efficiency practices | Mandatory plus ERV / HRV Ventilation required with minimum of 10 points in category |  | Mandatory Practices Required, Plus 10 Points | 32 | 100
|  |  | CZ 4 | 43
|  |  | CZ 5 | 44
|  |  | CZ 6 | 43
|  |  | CZ 7 | 42
Dual-Certification with Home Innovation Research Labs, LEED, DOE ZERO ENERGY READY HOME PROGRAM, AND EPA WATERSENSE PROGRAM
DUAL-CERTIFICATION REQUIREMENTS MUST STILL BE ADDRESSED
Next proceed to '2 Project Information' tab

## 2 Project Information
BGNM Certification Project Information
[5 empty] | Version 2015.05 (Dec 2015) |  |  | 0
Basic Project Data
Project Address: Enter the complete address as it should appear on the certificate. Use link for accurate address.
https://tools.usps.com/go/ZipLookupAction!input.action
Conditioned Floor Area:
Climate Zone (see '7 NM Climate Zones')
Number of Bedrooms:
Project Data for Determining Water Efficiency
Average rainfall (inches) |  |  |  | Detail of building lot area not under roof (sq. ft.):
Peak watering month |  |  |  | Landscape/softscape area (sq. ft.) |  |  | #DIV/0!
Evapotranspiration factor (Eto)) |  |  |  | Permeable paved area (sq. ft.) |  |  | #DIV/0!
Water cost ($/1000 gallons) |  |  |  | Directed impervious paved area (sq. ft.) |  |  | #DIV/0!
Sewer cost ($/1000 gallons) |  |  |  | Remaining impervious area (sq. ft.) |  |  | #DIV/0!
Lot size (sq. ft.) |  |  |  | Other surface areas (sq. ft.) |  |  | #DIV/0!
Building area under roof (sq. ft.) |  |  |  | Total lot area not under roof (must be 100%) |  | 0 | #DIV/0!
Remaining lot area not under roof (sq. ft.) |  |  | 0
Contact Information
Builder Information
Full Business Name
Complete Mailing Address
Contact Person
Phone Number
Email Address
HERS Rater Information |  |  | HERS Rater must be certified by and in good standing with RESNET.
HERS Rater Company Name
HERS Rater Name
Phone Number
Email Address
Green Verifier Information |  |  | Green Verifier must be certified by and be in good standing with Home Innovation Research Labs.
Green Verifier Company Name
Green Verifier Name
Phone Number
Email Address
Mailing Address for Final BGNM Certificate |  |  | Whose address is this?
To Attention of
Street Address 1
Street Address 2
City, State & Postal Zip Code
Email Address of Recipient
Documentation and Other Requirements for Certification
1 | Photos showing front and rear elevations of home showing as much of the landscape area as possible in the photos. Photos should be in PDF format (preferably) or JPG format.
2 | PDF of '2 Project Information' page
3 | Signed '3 Scoring & Verification' page in PDF format signed & sent by Verifier (electronic signature is okay).
4 | PDF of '6 Thermal Enclosure Checklist' page (or approved substitute) sent by HERS Rater or Verifier.
5 | PDF of '4 WEiR Index' page sent by Green Verifier.
6 | PDF of final confirmed Home Energy Rating Certificate (HERC) from HERS Rater.
7 | PDF of Home Energy Rating Certificate (HERC) without solar photovoltaics or wind energy generation from HERS Rater.
8 | PDF of Air Leakage Report from HERS Rater.
9 | PDF of 2009 IECC Energy Cost Compliance report from HERS Rater.
10 | PDF of 2015 IECC Energy UA Compliance report from HERS Rater if points taken for practice 1.4.3.
11 | Signed HVAC Accountability Form (Electronic Signatures allowed)
12 | Certification fee is due before submission of documents. Receipt from BGNM evidencing certification fee was paid to BGNM should be submitted in PDF form to prevent delay in processing the certification.
BGNM Registration Fee | [5 empty] | 50
BGNM Certification Fee | [5 empty] | 245
To register project go to https://certifiedgreennm.org/purchase-registrations-and-certifications/. The fee for registering a project is $50. Registration and certification fees must be paid before the project can be certified. Registration and certification fees can be made by credit card at https://certifiedgreennm.org/purchase-registrations-and-certifications/, or an invoice can be emailed to contact person upon registration of project.
Important Information about the Tabs in this Workbook
1 BGNM Program Overview |  | General overview of the certification program and requirements for each certification level.
2 Project Information |  | Information required by BGNM for certification. Must have at least the 'Conditioned Floor Area', 'Climate Zone', and '# of Bedrooms' filled out to start initial scoring of the project.
3 Scoring & Verification |  | This is the main tab for 'Points Claimed' scoring by the builder and 'Points Awarded' scoring by the HERS Rater/Green Verifier.
4 WEiR Index |  | Indoor Water Efficiency Rating System (WEiR) for initial scoring by Builder and verification by Green Verifier. Completion of this tab is required to populate the beginning of the Water Efficiency section of tab '3 Scoring & Verification'.
5 HVAC Accountability Form |  | Some practices require builder, subcontractor or supplier sign-off for points. All sign-offs may be done electronically through the builder.
6 Thermal Enclosure Checklist |  | Thermal Bypass Checklist. This form, or an approved substitute, must be submitted for certification.
7 NM Climate Zones |  | This tab provides the Climate Zones of each city. This is the source for cell E12 of tab '2 Project Information' and is used to determine the HERS index required for certification at each certification level.
8 IECC Insulation Requirements |  | This tab provides the information for practice 1.4.3 on tab '3 Scoring & Verification' for insulation and fenestration required by the 2015 International Energy Conservation Code (IECC).
Errata |  | This tab summarizes corrections and changes to this workbook from version to version.
To start scoring or verification proceed to '3 Scoring & Verification' tab

## 3 Scoring & Verification
Practice # | Building Practice | [8 empty] | Points Available | Points Claimed | Points Awarded | Notes About How Practice Is Satisfied |  | DO NOT DELETE THESE COLUMNS
|  | DATA INPUT Cells with this background color & red cells are data input cells |  |  |  | Project Address: | [7 empty] | Significant Attributes of Project
[6 empty] | (from '2 Project Information' page) | [7 empty] | Climate Zone
Conditioned Floor Area
|  | Version 2015.05 (Dec 2015) | [11 empty] | Number of Bedrooms
1 -- ENERGY EFFICIENCY
1.1 - HERS Index
| HERS Index Requirements by Certification Level and Climate Zone | [11 empty] | These minimum HERS indexes are required for certification for the various certification levels and climate zones.
| Certification Level ↓ Climate Zone → |  |  | CZ 3 | CZ 4 | CZ 5 | CZ 6 | CZ 7
| Bronze |  |  | 70 | 70 | 70 | 70 | 70
| Silver |  |  | 60 | 60 | 60 | 60 | 60
| Gold |  |  | 51 | 54 | 55 | 54 | 53
| Emerald |  |  | 41 | 43 | 44 | 43 | 42
1.1.1 | Mandatory HERS Index WITHOUT photovoltaics or wind: This HERS index requirement is to ensure that the thermal enclosure of the home provides a high level of energy efficiency before further HERS index improvements with solar photovoltaics or wind. | [8 empty] | MANDATORY No Points | Projected HERS Index WITHOUT solar photovoltaics or wind ↓ | Confirmed HERS Index WITHOUT solar photovoltaics or wind ↓ | HERS rater shall provide copy of Home Energy Rating Certificate (HERC) without solar photovoltaics or other forms of on-site energy production. The HERS index should be entered in the green (or red) input cells to the left.
| Certification Level |  |  | CZ 3 | CZ 4 | CZ 5 | CZ 6 | CZ 7
| Bronze |  |  | 70 | 70 | 70 | 70 | 70
| Silver, Gold and Emerald |  |  | 60 | 60 | 60 | 60 | 60
HIDE THIS ROW BUT DO NOT DELETE THIS ROW | [10 empty] | HERS Index? | HERS Index?
1.1.2 | Additional points for Silver, Gold and Emerald levels of certification if HERS index is less than 60, up to a maximum of 25 additional points. A better HERS index resulting from solar photovoltaics or wind can be used to earn these points. RESNET-certified HERS rater shall provide copy of Home Energy Rating Certificate for as-built home showing RESNET Registry ID number. Points will be automatically calculated based on the HERS index entered. | [8 empty] | 0.5 Point/HERS Index Point Below 60, 25 Maximum | Projected HERS index WITH all energy-related features is ↓ | Confirmed HERS index WITH all energy-related features is ↓
| Certification Level |  |  | CZ 3 | CZ 4 | CZ 5 | CZ 6 | CZ 7 |  | Points Earned → | 0 | 0
DO NO DELETE THESE ROWS | Bronze |  |  | 70 | 70 | 70 | 70 | 70
| Silver |  |  | 60 | 60 | 60 | 60 | 60
| Gold |  |  | 51 | 54 | 55 | 54 | 53
| Emerald |  |  | 41 | 43 | 44 | 43 | 42
1.2 - Space Heating and Space Cooling
1.2.1 | Equipment sizing. Space heating and space cooling systems shall be sized in accordance with ACCA Manual S based on building loads calculated in accordance with ACCA Manual J, or other approved heating and cooling equipment sizing methodologies. | [8 empty] | Mandatory |  |  | Complete and submit HVAC Accountability Form at tab 5.
1.2.2 | Heating and cooling distribution systems. Space heating and cooling distribution systems shall be designed and installed following the practices below, if applicable: | [9 empty] | Signed Accountability Form Required | Signed Accountability Form Required | Complete and submit HVAC Accountability Form at tab 5.
| (a) Heating and cooling distribution systems using ducting shall be sized and designed in accordance with ACCA Manual D, or equivalent. Heating and cooling distribution systems not requiring ducting shall be designed following appropriate industry guidelines and practices. | [8 empty] | Mandatory |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (b) All forced air space heating and space cooling duct distribution systems shall be air-sealed. All duct sealing materials shall be in conformance with UL181A or UL181B specifications and shall be installed in accordance with manufacturer's instructions. | [8 empty] | Mandatory |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (c) Building cavities shall not be used as supply or return ducts. Industry-approved duct materials shall be used to minimize leakage of conditioned air. This includes plenums such as platforms under forced air systems for return air. All such cavities shall be lined and sealed with appropriate duct materials. | [8 empty] | Mandatory |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (d) Boiler supply piping and domestic hot water supply piping located in unconditioned spaces shall be insulated to R-3 or higher | [8 empty] | Mandatory |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (e) A return air path shall be provided for every room with a door (i.e. return ducts or transfer grills) for forced-air heating and cooling distribution systems. Return ducts or transfer grills are not required for bathrooms, kitchens, closets, pantries, and laundry rooms. | [8 empty] | 1 |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (f) Balanced HVAC airflows are demonstrated by flow hood or other acceptable flow measurement tool by a third party. Test results are confirmed by both of the following required documents: a Manual D report and an Accountability Report evidencing the results of the testing is provided to the third-party verifier. (1) Measured flow at each supply and return register is within 25% of design flow, OR (2) Total airflow is within 10 percent of design flow | [8 empty] | 2 |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (g) All space heating and space cooling is provided by system(s) that does not require air distribution ducting | [8 empty] | 3 |  |  | Complete and submit HVAC Accountability Form at tab 5.
1.2.3 | HVAC system performance testing. Performance of the heating and cooling systems is verified by the HVAC contractor in accordance with all of the following, if applicable, and the Accountability Form for HVAC System Performance Testing is provided to the verifier: | [9 empty] | Signed Accountability Form Required | Signed Accountability Form Required | Complete and submit HVAC Accountability Form at tab 5.
| (a) Start-up procedure is performed in accordance with the manufacturer's instructions | [8 empty] | Mandatory |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (b) Burner is set to fire at input level listed on nameplate (combustion equipment) | [8 empty] | Mandatory |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (c) Refrigerant charge is verified by super-heat and/or sub-cooling method | [8 empty] | 0.5 |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (d) Air handler settings and fan speed(s) are set in accordance with manufacturer's instructions | [8 empty] | 0.5 |  |  | Complete and submit HVAC Accountability Form at tab 5.
| (e) Duct leakage testing is performed by third-party verifier per RESNET protocol demonstrating that the entire air distribution system including ducts, air handlers and register boots has measured duct leakage to outside at a pressure differential of 25 Pascals of no greater than 4 CFM per 100 square feet of conditioned floor area. | [8 empty] | 0.5 |  |  | Complete and submit HVAC Accountability Form at tab 5.
1.2.4 | HVAC contractor and service technician are certified. Nationally or regionally recognized program (e.g. North American Technician Excellence, Inc. (NATE), Air Conditioning Contractors of America's Quality Assured Program (ACCA/QA), Building Performance Institute (BPI), or a manufacturer's training program is acceptable. The Accountability Form for Certification of HVAC contractor and technician shall be provided. | [8 empty] | 1 |  |  | Complete and submit HVAC Accountability Form at tab 5.
1.3 - Fenestration
1.3.1 | Skylights and tubular daylighting devices. Skylights or tubular daylighting devices installed in areas/rooms without windows OR areas/rooms without windows equipped with motion and light sensors to automatically turn lighting on if ambient light is low and the space is occupied and turn lighting off if the space is not occupied. | [8 empty] | 1
1.4 - Air Sealing and Insulation
1.4.1 | Thermal Enclosure Checklist. BGNM requires that '6 Thermal Enclosure Checklist', or a substantially similar checklist approved by BGNM, be completed. Note that the checklist must be prepared by the Verifier and submitted to both the builder and BGNM. See '6 Thermal Enclosure Checklist' for form. | [8 empty] | Mandatory |  |  | Note that it is mandatory to provide the Thermal Enclosure Checklist. This is an educational tool for builders and reinspection is not required if a Thermal Enclosure Checklist practice is not met.
1.4.2 | Building enclosure leakage testing. A blower door test is performed by a third-party in accordance with RESNET protocols. The blower test result in air changes per hour at 50 Pascals pressure difference (ACH50) is reported and additional points awarded for superior building enclosure air-tightness in accordance with the table below. | [8 empty] | Zero or 2 | Enter ACH50 Below | Enter ACH50 Below
| 3.0 ACH50 or greater |  | No Points | [7 empty] | Projected ACH50 ↓ | Tested ACH50 ↓
| Less than 3.0 ACH50 |  | 2 Points
1.4.3 | Insulation levels, including fenestration specifications, meet or exceed the requirements of the 2015 IECC. If points are taken, provide copy of 2015 IECC Building UA Compliance report. See '8 IECC Insulation Requirements' page for more detail. | [8 empty] | 1
1.5 - Other Energy Efficiency Practices
1.5.1 | Energy consumption control. A whole-building or whole-dwelling unit device is installed that controls or monitors energy consumption, as shown below (1 point each): (a) Programmable communicating thermostat (b) Energy-monitoring device (c) Energy management control system | [8 empty] | Maximum of 2
1.5.2 | Passive cooling design, including at least 3 of the following practices: | [8 empty] | 2
(a) At least 75% shading of east and west facing windows using physical structures or vegetation
(b) South-facing glass shall be shaded in accordance with the following table that shows the required south-facing window overhang depth:
Vertical Distance Between Bottom of Overhang and Top of Window Sill
|  | ≤ 7'-4" | ≤ 6'-4" | ≤ 5'-4" | ≤ 4'-4" | ≤ 3'-4"
| Climate Zone 3 Overhang Depth | 2'-8" | 2'-8" | 2'-4" | 2'-0" | 2'-0"
| Climate Zones 4, 5 & 6 Overhang Depth | 2'-4" | 2'-4" | 2'-0" | 2'-0" | 1'-8"
| Climate Zone 7 Overhang Depth | 2'-0" | 1'-8" | 1'-8" | 1'-4" | 1'-0"
(c) Cross-ventilation is provided using appropriately placed windows and/or skylights
(d) Solar-reflective roof or radiant barrier is installed in CZ 3
(e) Internal exposed thermal mass of at least three inches thick with a minimum of one-third of gross finished floor area
1.5.3 | Passive heating design, including all of the following practices: | [8 empty] | 0 |  |  | SV ADDED THIS PRACTICE AFTER THE LAST WORKING GROUP MEETING WITHOUT CONSULTATION WITH THE WORKING GROUP. THE WORKING GROUP MUST OPINE ON THIS PRACTICE. SV SUBSEQUENTLY SPOKE TO SH & LEARNED SH INTENTIONALLY DID NOT INCLUDE PASSIVE HEATING DESIGN BECAUSE THIS IS ALREADY WELL ACCOUNTED FOR IN THE HERS INDEX. SV AGREES SO THIS PRACTICE IS BEING HIDDEN AND NOT USED. The practice is from NGBS 703.6.4 and is considered valuable particularly in CZs 5, 6 & 7.
a. The longest side of the home faces within 20 degrees of true south
b. Vertical glazing meets the following requirements: (1) South (135⁰-225⁰): 5%-12% of CFA on south side and SHGC of ≥ 0.40; (2) West (225⁰-315⁰): < 2% of CFA on west side; (3) East (45⁰-135⁰): < 4% of CFA on east side; and (4) North (315⁰-45⁰): < 8% of CFA on north side.
c. Skylights, when installed, meet the following requirements: (1) skylight shafts and curbs above roof deck are insulated to ≥ R-15; (2) horizontal skylights are , 0.5% of ceiling area; (3) sloped skylights within 45⁰ of true south, east or west are < 1.5% of ceiling area
d. South-facing glass shall be shaded in accordance with the following table:
Vertical Distance Between Bottom of Overhang and Top of Window Sill
|  | ≤ 7'-4" | ≤ 6'-4" | ≤ 5'-4" | ≤ 4'-4" | ≤ 3'-4"
| Climate Zone 3 Overhang Depth | 2'-8" | 2'-8" | 2'-4" | 2'-0" | 2'-0"
| Climate Zones 4, 5 & 6 Overhang Depth | 2'-4" | 2'-4" | 2'-0" | 2'-0" | 1'-8"
| Climate Zone 7 Overhang Depth | 2'-0" | 1'-8" | 1'-8" | 1'-4" | 1'-0"
e. Additional internal exposed thermal mass in any room with south-facing glazing of at least 3" thick: (1) thermal mass directly exposed to sunlight - 5 sq. ft. of thermal mass for every 1 sq. ft. of south-facing glazing, or (2) thermal mass not directly exposed to sunlight - 40 sq. ft. of thermal mass for every 1 sq. ft. of south-facing glazing.
1 -- ENERGY EFFICIENCY - TOTAL POINTS | [9 empty] | 38.5 | 0 | 0
Certification Status in Energy Efficiency Section:
(a) | HERS Index emphasizing thermal enclosure system (without on-site energy generation) | [9 empty] | Must enter HERS index above | Must enter HERS index | Dependent on climate zone and certification level |  | 0 | 0
(b) | HERS Index with on-site energy generation qualifies for this certification level | [9 empty] | HERS Index? | HERS Index? | Dependent on climate zone and certification level |  | 0 | 0
(c) | Mandatory practices met? | [9 empty] | Satisfied | Satisfied |  |  | 4 | 4
(e) | OVERALL CERTIFICATION LEVEL ACHIEVED FOR ENERGY EFFICIENCY SECTION | [9 empty] | CANNOT CERTIFY | CANNOT CERTIFY | Certification level achieved for this section. Note that the overall certification level for energy efficiency cannot be greater than any of the specific levels achieved above.
2 -- WATER EFFICIENCY
2.1 - Indoor Water Use Efficiency Practices
2.1.1 | WEiR index points for indoor water use. Points awarded equal 100 less the WEiR index achieved. WaterSense water fixtures and ENERGY STAR water appliances set the minimum WEiR Index. Complete the WEiR Index spreadsheet to tabulate the score. | [5 empty] | WEiR Index from WEiR Index spreadsheet | [5 empty] | See details & specifications on WEiR Index sheet
2.1.2 | Domestic hot water distribution systems with circulation pumps. | [8 empty] | 1 |  |  | Describe hot water recirculation system below:
(a) On-demand circulation systems serving ALL hot water fixtures -- allow 1 point
(b) Circulation systems that are not on-demand and are controlled by timer and/or aquastat -- deduct 1 point
(c) Circulation systems that are constantly on -- deduct 2 points
2.2 - Outdoor Water Use Efficiency Practices
2.2.1 | Landscape Plants. At least 80% (by area) of plants installed in the landscape, including turf grass, shrubs, trees and all other plants, must be appropriate for the region as determined by the local water authority or be on the plant list issued by the State Engineer's office at http://wuc.ose.state.nm.us/Plants/ or local water authority if available. (Vegetable gardens and fruit trees exempt). | [11 empty] | Verifier must provide lists of predominant regionally-appropriate plants used in the landscape in the Notes below if points are taken for these practices.
| (a) Front is landscaped with 80% low water use plantings meeting the requirements described above, and turf grass cannot exceed 10% of the front yard area | [8 empty] | 2
| (b) Back is landscaped with overall low water use plantings and ground cover with turf not exceeding 1500 sf or 20% (whichever is less) of total landscape area (front and back) | [8 empty] | 2
| (c) Native landscaping requiring no irrigation after being established is used for the entire landscape. Points cannot be awarded for this practice if points awarded for either of 2.2.1(a) or 2.2.1(b). | [8 empty] | 4
2.2.2 | Irrigation System. Points may be awarded for the following landscape irrigation practices:
| (a) Irrigation system water supply is stubbed for front and rear landscape irrigation with either a power supply or wiring for irrigation valve controls provided | [8 empty] | 1
| (b) Automatic sprinkler and drip irrigation controls are installed and cover 80% or more of new plants and turf (1.5 points front, 1.5 points rear, 3 point both) | [8 empty] | 1.5, Max 3
| (c) Rain sensor or soil moisture sensor is part of Irrigation controls | [8 empty] | 1
2.3 - Water Capture and Re-use
2.3.1 | Rainwater is diverted or captured for beneficial use on the property.
| (a) Rainwater is captured in storage tank for reuse at .5 point per 200 gallons storage up to 5 points | [8 empty] | 0 - 5.0
| (b) Rainwater is diverted by gravity to planted swales for direct use (.5 point per 25% of remaining covered roof area not used for rainwater storage capture ) | [8 empty] | 0 - 2.0
2.3.2 | Greywater (or other waste water) from indoor use is diverted or captured for reuse in a safe and approved manner. These points are automatically calculated from information entered on the '4 WEiR Index' sheet. | [8 empty] | 5 | 0 | 0 | These points are automatically calculated based on information input on '4 WEiR Index' sheet.
2.4 - Other Water Efficiency Practices
2.4.1 | Automatic shutoff water device. One of the following automatic shutoff water supply devices is installed. Where a fire sprinkler system is present, installer is to ensure the device will not interfere with the operation of the fire sprinkler system. | [8 empty] | 1
(a) Excess water flow automatic shutoff OR
(b) Leak detection system with automatic shutoff
2.4.2 | Replace old inefficient toilets with new efficient toilets. Replace one or more toilets that use at least 3.5 gallons per flush in existing home(s) with toilets using no more than 1.28 gallons per flush. Toilet replacements can be made in other homes. Builder must provide evidence of replacement. | [8 empty] | 3
2.4.3 | Evaporative cooling system(s). Space cooling is accomplished with an evaporative cooling system that uses no more than 3.5 gallons of water per ton-hour of cooling capacity and a maximum of 3 water flushes (blow-downs) for reducing mineral and salt buildup per 24-hour period. Controls water flushes through conductivity or a basin temperature-based controller. Contact BGNM for information about how to score. | [8 empty] | Points to be determined by BGNM |  |  | MUST DETERMINE POINTS AND PROVIDE INFORMATION ABOUT HOW TO ACCOMPLISH THE PRACTICE
2.4.4 | Water softener systems. Certified to NSF/ANSI Standard 44, including voluntary efficiency rating standards in Section 7 of that standard. Contact BGNM for information about how to score. | [8 empty] | Points to be determined by BGNM |  |  | Not verified because points are not needed for desired certification level.
2.4.5 | Drinking water treatment system. System must be NSF/ANSI certified with a minimum efficiency rating of 85%. Contact BGNM for information about how to score. | [8 empty] | Points to be determined by BGNM |  |  | MUST DETERMINE POINTS AND PROVIDE INFORMATION ABOUT HOW TO ACCOMPLISH THE PRACTICE
2.4.6 | Recycled water used for clothes washing. Contact BGNM about how to score. | [8 empty] | Points to be determined by BGNM |  |  | MUST DETERMINE POINTS AND PROVIDE INFORMATION ABOUT HOW TO ACCOMPLISH THE PRACTICE
2.4.7 | Hands free faucets installed in kitchen and lavatories. | [8 empty] | 1
2.4.8 | Water shutoff mechanism is installed on showerheads to automatically decrease water flow to showerhead to <= 8 ounces/minute when the water temperature at the showerhead reaches => 95° and which allows occupant to 'switch' the showerhead flow to normal flow when ready for shower. Allow 0.5 points per showerhead up to maximum of 1 point. | [8 empty] | 0 - 1.0
2.4.9 | Water treatment backflush water beneficially reused. | [8 empty] | 0.5
2.4.10 | Water use monitoring system is installed. | [8 empty] | 1
2.4.11 | Greywater stubout. | [8 empty] | 2
2.4.12 | Purple pipe stubout. | [8 empty] | 2
2.4.13 | Water leakage testing completed and results available for builder or homeowner. (For data collection purposes) | [8 empty] | 1
2 -- WATERY EFFICIENCY - TOTAL POINTS | [9 empty] | 130 | 0 | 0
Certification Status in Water Efficiency Section:
(a) | Highest level of certification achievable based on WEiR index | [9 empty] | WEiR Index? | WEiR Index? | Dependent on WEiR index & certification level |  | 0 | 0
(b) | Mandatory practices met? | [9 empty] | Not Applicable | Not Applicable | Currently there are no mandatory practices in this section |  | 99 | 99
(c) | Total points achieved in this section qualify for this certification level in this section | [9 empty] | Bronze | Bronze | Highest certification level that can be achieved based on points awarded in this section |  | 1 | 1
(d) | OVERALL CERTIFICATION LEVEL ACHIEVED FOR WATER EFFICIENCY SECTION | [9 empty] | CANNOT CERTIFY | CANNOT CERTIFY | Certification level achieved for this section
3 -- INDOOR AIR QUALITY
3.1 - Spot Ventilation (Minimize potential for mold or other irritants resulting from condensation or water intrusion)
3.1.1 | Spot ventilation is provided as described below:
| (a) Clothes dryers are vented to the outdoors. | [8 empty] | Mandatory
| (b) Bathroom and laundry fans are vented to the outdoors. Fans shall be tested and verified to have a minimum ventilation rate of 50 cfm for intermittent operation or 20 cfm for continuous operation. Results to be listed in notes column. | [8 empty] | Mandatory
| (c) Kitchen has exhaust fans and range hoods are ducted to the outside. (Mandatory) Kitchen Exhaust fan is tested and verified to meet requirements (1 point if verified to vent => 100 cfm). Result to be listed in notes column. | [8 empty] | Mandatory 1 Point if CFM Verified
| (d) Humidistat, timer, motion sensor or part of whole-house ventilation in master AND 1 other bath minimum | [8 empty] | 1
| (e) Exhaust fans are Energy Star rated (1 point per fan max 2 pts) | [8 empty] | 2
| (f) Exhaust fans are Energy Star rated and operate at 1 sone or less (1 point per 2 fans with 2 pts max) | [8 empty] | 2
3.2 - Whole building ventilation systems
3.2.1 | Whole building ventilation is implemented in accordance with ASHRAE 62.2-2010 using the following calculation or other calculation meeting the requirements of ASHRAE 62.2-2010 if the air infiltration leakage as determined for practice 1.4.2 above is 7.0 ACH50 or less: | [8 empty] | Mandatory (if building leakage test is 7.0 ACH50, or less) | Projected Whole Building Ventilation in CFM ↓ | Tested Whole Building Ventilation in CFM ↓
Required whole building ventilation (in CFM) = (Conditioned Floor Area ÷ 100) + [7.5 x (Number of Bedrooms + 1)]
| Required whole building ventilation (in CFM) = |  |  |  | #VALUE! | [5 empty] | #VALUE! | #VALUE!
| (a) Exhaust or supply only system tested and meeting ASHRAE 62.2-2010 whole-house ventilation requirements described above. | [8 empty] | 1
| (b) Balanced exhaust and supply fans tested and meeting ASHRAE 62.2-2010 whole-house ventilation requirements described above. | [8 empty] | 2
| (c) ERV or HRV system installed and tested and meeting ASHRAE 62.2-2010 whole-house ventilation requirements described above. | [8 empty] | 4
3.3 - Space Heating and Water Heating Options
3.3.1 | Space Heat and Water Heating locations. Natural draft furnaces, boilers and water heaters located in conditioned space are in a sealed mechanical room that has an outdoor air source, sealed and insulated from the conditioned space | [8 empty] | Mandatory
3.3.2 | Return ductwork and air handling equipment is not located in the garage unless placed in sealed mechanical room that has an outdoor air source. A framed plenum under furnace must be ducted and sealed with approved ducting material. | [8 empty] | Mandatory
3.3.3 | Heating equipment is direct vent or power vent. | [8 empty] | 2
3.3.4 | Air filters installed on central forced air systems of MERV 8 or greater and or pleated filter with a MPR rating of 600 or greater and HVAC supplier verifies system to accommodate the larger pressure drop. Must meet energy spec for pressure drop. | [8 empty] | 1
3.3.5 | Water heating equipment is direct vent or power vent. | [8 empty] | 1
3.3.6 | Supply and return openings are covered during construction or vacuumed before occupancy by builder; spot check by verifier for compliance. | [8 empty] | Mandatory
3.4 - Solid fuel-burning appliances
3.4.1 | Gas fireplaces and direct heating equipment is listed and is installed in accordance with the NFPA National Fuel Gas Code or ICC International Fuel Gas Code or the applicable local gas appliance installation code. Gas fired fireplaces and direct heating equipment are vented to the outdoors. | [8 empty] | Mandatory
3.4.2 | Gas fireplaces are direct vented and have permanently fixed glass fronts or gasketed doors and comply with CSA ANSI Z21.88 or CSA ANSI Z21.50b / CSA 2.22b. | [8 empty] | Mandatory
3.4.3 | Site built masonry wood burning fireplaces are equipped with outside combustion air and a means of sealing the flue and the combustion air outlets to minimize interior air (heat) loss when not in operation. | [8 empty] | Mandatory
3.4.4 | Manufactured fireplaces, wood stoves and pellet stoves are in compliance with appropriate requirements and follow emission requirements of the EPA per their category. | [8 empty] | Mandatory
3.4.5 | No fireplace, wood stove, pellet stove or masonry heater is installed. | [8 empty] | 2
3.5 - Garages
3.5.1 | A 100 cfm or greater exhaust fan is installed and vented to the outdoors, and is designed for continuous operation or has controls to activate and run for 1 hour each time the garage door is operated. | [8 empty] | 1
3.5.2 | A carport is installed, the garage is detached from the building or no garage is installed. | [8 empty] | 2
3.6 - Carbon Monoxide and Radon Gas
3.6.1 | CO alarm is installed per IRC 3.15 | [8 empty] | Mandatory
3.6.2 | CO monitors are installed. (Note: a basic CO alarm is NOT a CO monitor.) | [8 empty] | 1
3.6.3 | For Radon Zone 1, a passive or active radon mitigation system is installed with description detailed in the owner's manual. | [8 empty] | Mandatory
3.6.4 | For Radon Zones 2 and 3, a passive or active radon mitigation system is installed with description detailed in the owner's manual. | [8 empty] | 1
3.7 - Materials
3.7.1 | Structural plywood. Structural plywood used for floor, wall, and/or roof sheathing is compliant with DOC PS1 and/or DOC PS 2. OSB used for floor, wall, and/or roof sheathing is compliant with DOC PS 2. The panels are made with moisture-resistant adhesives. The trademark indicates these adhesives as follows: Exposure 1 or Exterior for plywood, and Exposure 1 for OSB. | [8 empty] | Mandatory
3.7.2 | Wood Materials. For each product group below, a minimum of 85% of material within the product group is manufactured in accordance with the following requirements for the wood product groups: • Particleboard and MDF (medium density fiberboard) is manufactured and labeled in accordance with CPA A208.1 and CPA A208.2, respectively. • Hardwood plywood in accordance with HPVA HP-1. • Particleboard, MDF, or hardwood plywood is in accordance with CPA4. • Composite wood or agrifiber panel products contain no added urea-formaldehyde or are in accordance with the CARB Composite Wood Air Toxic Contaminant Measure Standard. • Non-emitting products. | [9 empty] | Builder must have documentation available for verifier if claiming points for these practices
| (a) Counter tops | [8 empty] | 0.5
| (b) Composite trim | [8 empty] | 0.5
| (c) Custom wood work | [8 empty] | 0.5
| (d) Shelving | [8 empty] | 0.5
3.7.3 | Cabinets. A minimum of 85% of installed cabinets are in accordance with one or both of the following: | [9 empty] | Builder must have documentation available for verifier if claiming points for these practices
| (a) All parts of the cabinet are made of solid wood or non-formaldehyde emitting materials such as metal or glass. | [8 empty] | 0.5
| (b) Composite wood used in wood cabinets is certified by KCMA, ESP or an equivalent program evidencing very low or no formaldehyde emissions. | [8 empty] | 0.5
3.7.4 | Carpets. Carpets are in accordance with the following:
| (a) Carpet is not installed in wet areas around tubs, toilets or showers | [8 empty] | Mandatory
| (b) Carpets are third-party program certified to ISO Guide 65 (i.e. CRI Green Label Plus). Builder must provide verifier documentation support. | [8 empty] | 0.5
3.7.5 | Hard-surface flooring. Prefinished hard-surface flooring is installed that is third-party program certified to ISO Guide 65 (i.e. GREENGUARD Environmental Institute Children & Schools Certification Program or Resilient Floor Covering Institute’s Floor Score Indoor Air Certification Program) OR, if sealed on-site, the coating meets the requirements of 3.7.6. | [9 empty] | Builder must have documentation available for verifier if claiming points for these practices
| (a) Hard surface flooring meeting these requirements covers 20% to 50% of conditioned floor area, or | [8 empty] | 0.5
| (b) Hard surface flooring meeting these requirements covers more than 50% of conditioned floor area. | [8 empty] | 1
3.7.6 | Interior architectural coatings. A minimum of 85% of interior (within the air pressure boundary of the home) architectural coatings are in accordance with the following maximum VOC content (allow 0.5 points per category, up to maximum of 1.5 points): | [8 empty] | 1.5 | Builder must have documentation available for verifier if claiming points for these practices |  | Document below the percentage of area treated with compliant interior architectural coatings and list the coatings and their VOC content.
(a) GreenSeal GS-11 certified - any interior architectural coating
(b) Zero VOC as determined by EPA Method 24 - any interior architectural coating
(c) Flat paint - 50 grams/liter
(d) Non-flat paint - 100 grams/liter
(e) Non-flat high-gloss paint - 150 grams/liter
(f) Faux finish coatings - 350 grams/liter
(g) Fire resistive coatings - 350 grams/liter
(h) Floor coatings - 100 grams/liter
(i) Primers, sealers and undercoatings - 100 grams/liter
(j) Rust preventative coatings - 250 grams/liter
(k) Concrete or masonry sealers - 100 grams/liter
(l) Shellacs, clear - 730 grams/liter
(m) Stains - 250 grams/liter
(n) Waterproofing membranes - 250 grams/liter
(o) Wood coatings - 275 grams/liter
3.7.7 | Interior adhesives and sealants. A minimum of 85% of site-applied interior (within the air pressure boundary ) adhesives and sealants are in accordance with the following maximum VOC content or are GreenSeal GS-36 certified (0.5 point for each product category, up to maximum of 2 points): | [8 empty] | 2 | Builder must have documentation available for verifier if claiming points for these practices |  | Document below the percentage of interior adhesives & sealants and list the interior adhesives & sealants and their VOC content.
| (a) Indoor carpet pad & carpet adhesives or sealants - 50 grams/liter | [9 empty] | Number of compliant product categories ↓ | Number of compliant product categories ↓
(b) Wood flooring adhesives - 100 grams/liter
(c) Subfloor adhesives - 50 grams/liter
(d) Ceramic tile adhesives - 65 grams/liter
| (e) Drywall and panel adhesives - 50 grams/liter | [9 empty] | 0 | 0
3.7.8 | Insulation. A minimum of 85% of wall, ceiling and floor insulation materials are third-party program certified to ISO Guide 65, such as, but not limited to, GREENGUARD Environmental Institute Children and Schools Certification Program or Scientific Certification Systems (SCS) Indoor Advantage Gold Program. | [8 empty] | 1 | Builder must have documentation available for verifier if claiming points for these practices |  | Document below the percentage of insulation in compliance with the requirements and list the insulation products used and the certification program used for certification.
3.8 - Other Indoor Air Quality Practices
3.8.1 | Central vacuum system is installed and vented to the outside | [8 empty] | 1
3 -- INDOOR AIR QUALITY - TOTAL POINTS | [9 empty] | 30 | 0 | 0
Certification Status in Indoor Air Quality Section:
(a) | Mandatory practices met? | [9 empty] | #VALUE! | #VALUE! |  |  | #VALUE! | #VALUE!
(b) | Total points achieved in this section qualify for this certification level in this section | [9 empty] | Silver | Silver | Highest certification level that can be achieved based on points awarded in this section. |  | 2 | 2
(c) | ERV or HRV installed? | [9 empty] | No | No | An HRV or ERV is required for Emerald Certification |  | 3 | 3
(d) | OVERALL CERTIFICATION LEVEL ACHIEVED FOR INDOOR AIR QUALITY SECTION | [9 empty] | #VALUE! | #VALUE! | Certification level achieved for this section
4 -- SUSTAINABILITY
4.1 | D.O.E. Benchmark Home Size Adjustment: The DOE benchmark home size is based on the number of bedrooms as shown in the table below. BGNM awards or penalizes building home sizes at 1 point for each 300 square feet above or below the DOE Benchmark Home Size criteria. | [8 empty] | Penalty of 1 point for each 300 sf above benchmark, or add 1 point for each increment below
| Number of bedrooms |  | 0 | 1 | 2 | 3 | 4 | 5 | 6
| D.O.E. Benchmark Home Size - CFA |  | 1000 | 1000 | 1600 | 2200 | 2800 | 3400 | 4000
4.2 - Lot Design
4.2.1 | Limits of clearing and grading and any natural resources to be protected are fenced or otherwise marked off on the site. Adjacent lots, common areas are protected from damage. | [8 empty] | 1
4.2.2 | Impervious surfaces are minimized and permeable materials are used for driveways, walkways and patios. .5 point per 25% converted. | [8 empty] | 2
4.2.3 | A lot is selected in a Green Certified Subdivision (note certification program). | [8 empty] | 2
4.2.4 | An infill lot is selected with public infrastructure to the lot and six or more public resources within one mile (shops, library, restaurants, public transportation, schools, etc.). List resources in Notes column. | [8 empty] | 2
4.2.5 | An infill lot is selected that is a greyfield. Note former land use. | [8 empty] | 2
4.2.6 | Soil disturbance and erosion are minimized in accordance with a SWPPP plan. | [8 empty] | 1
4.2.7 | Soil density test is performed and certified for compliance to recommendations | [8 empty] | 2
4.2.8 | Density of seven dwelling units per acre or greater (1 point), 15 or greater (2 pts), or >20 DU per acre (3 pts). | [8 empty] | 3
4.2.9 | Wildlife habitat: plants and gardens that provide food or nesting for birds and/or butterflies. | [8 empty] | 1
4.2.10 | Wildlife habitat: outdoor lighting techniques (down lighting) are utilized with regard for "night sky" preservation. | [8 empty] | 1
4.3 - Durability
4.3.1 | Continuous physical foundation termite barrier or low toxicity treatment including all structural walls, floors, exterior claddings within the first 3 feet above the top of the foundation for termite protection is installed. | [8 empty] | 1
4.3.2 | Exterior doors are protected by an overhang with a minimum 0.375 projection factor. Eastern and western facing entries in Climate Zones 1, 2, and 3 have a projection factor 1.0 minimum. (PF = A/B; A = overhang depth, B = bottom of overhang to bottom of door) (1 point per covered door with a maximum of 4 points). | [8 empty] | 4
4.3.3 | Roof overhangs are 12" deep or enhanced waterproofing (extra waterproof layer of sheathing over drainage layer with no penetrations on top) is used on parapets. Builder to provide details for Verifier. | [8 empty] | 1
4.3.4 | A gutter and downspout system or splash blocks and effective grading are provided to carry water a minimum of five feet away from perimeter foundation walls. Finished grade is at all sides of a building is sloped to provide a minimum of six inches of fall within ten feet or 2% slope if less than ten feet. | [8 empty] | 1
4.4 - Recycling, Renewable and Engineered products
4.4.1 | Location for sorting of scrap and recycling of materials is provided. | [8 empty] | 1
4.4.2 | Construction materials are recycled offsite. At least 2 categories of materials should be recycled (metal, wood, cardboard/paper, plastic) Note material categories recycled. | [8 empty] | 1
4.4.3 | Home owner recycling is facilitated with recycling space in the kitchen and a collection space in the garage or other protected area on the property. | [8 empty] | 1
4.4.4 | Prefabricated components for
| (a) floor system | [8 empty] | 1
| (b) wall system | [8 empty] | 1
| (c) roof system | [8 empty] | 1
4.4.5 | Modular construction for home | [8 empty] | 3
4.5 - Universal Design
4.5.1 | No step entrance with minimum 32 inch wide clearance. | [8 empty] | 1
4.5.2 | 36 " minimum accessible route from no step entrance to visiting area. | [8 empty] | 1
4.5.3 | 36 " accessible route from no step entrance to bedroom and bathroom with minimum 32 inch door width. | [8 empty] | 1
4.5.4 | Blocking for grab bars for accessible bathroom is provided. | [8 empty] | 1
4.6 - Building Owner Education
4.6.1 | Placeholder for Build Green NM Certificate (to be provided by BGNM) and HERS Certificate. | [8 empty] | Provided By BGNM
4.6.2 | Label of BGNM certification for home (provided by Build Green NM) to be installed by owner or builder. | [8 empty] | Provided By BGNM
4.6.3 | Placeholder for Certification Checklist as verified and certified by Build Green NM (including builder claimed practices) . | [8 empty] | Provided By BGNM
4.6.4 | Documented location of all shut-offs for utilities. | [8 empty] | 0.5
4.6.5 | Maintenance checklist. | [8 empty] | 0.5
4.6.6 | Integrated pest management plan is developed and instructions for maintenance. | [8 empty] | 0.5
4 -- SUSTAINABILITY - TOTAL POINTS | [9 empty] | 43.5 | 0 | 0
Certification Status in Sustainability Section:
(a) | Mandatory practices met? | [9 empty] | NOT APPLICABLE | NOT APPLICABLE |  |  | 99 | 99
(b) | Total points achieved in this section qualify for this certification level in this section | [9 empty] | Silver | Silver | Highest certification level that can be achieved based on points awarded in this section. |  | 2 | 2
(c) | OVERALL CERTIFICATION LEVEL ACHIEVED FOR SUSTAINABILITY SECTION | [9 empty] | SILVER | SILVER | Certification level achieved for this section
TOTAL POINTS FOR ALL GREEN BUILDING PRACTICES | [9 empty] | 242 | 0 | 0
SUMMARY OF CERTIFICATION STATUS
Energy Efficiency Section -- Highest Certification Level Achieved | [10 empty] | CANNOT CERTIFY | CANNOT CERTIFY | Third-party Verified by: |  | 0 | 0
Water Efficiency Section -- Highest Certification Level Achieved | [10 empty] | CANNOT CERTIFY | CANNOT CERTIFY |  |  | 0 | 0
Indoor Air Quality Section -- Highest Certification Level Achieved | [10 empty] | #VALUE! | #VALUE! |  |  | #VALUE! | #VALUE!
Sustainability Section -- Highest Certification Level Achieved | [10 empty] | SILVER | SILVER | Signature of Verifier (Electronic Signature is Okay): |  | 2 | 2
Additional Points Required from Any Section -- Highest Certification Level Achieved | [10 empty] | Bronze | Bronze |  |  | 1 | 1
OVERALL -- Highest Certification Level Achieved | [10 empty] | #VALUE! | #VALUE!

## 4a WEiR Index
[9 empty] | hidden | hidden | hidden | hidden | hidden | hidden | hidden | hidden |  |  | hidden | hidden
|  |  |  | Version 2015.05 (Dec 2015) | [14 empty] | What is this column needed for? | What is this column needed for? | Indoor Water Efficiency Rating (WEiR)
Project Address: | [6 empty] | Number of bedrooms must be entered on '2 Project Information' tab before this sheet will tabulate properly.
(from '2 Project Information Page)
Indoor Water Fixtures and Appliances
| Water Fixture or Appliance | Notes (see below) | Industry Baseline | BGNM Baseline | Proposed (Preliminary) or Final Verification (Use average if various flow rates) | Fixture or Appliance Installed in Home? | Required for Grey Water Reuse Calculations |  | Number of Fixtures or Appliances (HIDDEN FOR BGNM) | Quantity Multiplier (If Column G = Yes) | Occupants | Frequency |  | Industry Baseline Gal/Day | BGNM Baseline Gal/Day | Proposed or Actual Daily Use in Gallons | Gallons saved | Percent Saved Per Fixture | EXPECTED Percent of Overall Use (AWWA) | ACTUAL Percent of Overall Use | Installation or Testing Confirmed? (For final certification, ALL rows below must be verified 'Yes'. | Notes About How Practice is Satisfied
[7 empty] | Total Number of Fixtures Installed | Number of Fixtures Plumbed for Grey Water Reuse |  |  | Occupants (Bedrooms +1) LINKED | Duration (minutes) LINKED | Uses/Day/Occupant LINKED
A | Toilets (GPF) | (a), (b) | 1.6 | 1.28 |  |  |  |  | 1 | 0 | 1 |  | 5 | 0 | 0 | 0 | 0 | 0% | 26.7% | #DIV/0!
B | Showerheads (GPM) | (a), (c) | 2.5 | 2 |  |  |  |  | 1 | 0 | 1 | 5 | 1 | 0 | 0 | 0 | 0 | 0% | 16.8% | #DIV/0!
C | Bathtubs | (k) | For Greywater Calcs
D | Lavatory Faucets (GPM) | (a), (d) | 2.2 | 1.5 |  |  |  |  | 1 | 0 | 1 | 0.25 | 5 | 0 | 0 | 0 | 0 | 0% | 7.7% | #DIV/0!
E | Kitchen Faucets (GPM) | (a), (e) | 2.2 | 2.2 |  |  |  |  | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0% | 8% | #DIV/0!
F | Dishwashers (GPC) | (f) | 6.5 | 4.25 |  |  |  |  | 1 | 0 |  |  | 1 | 0 | 0 | 0 | 0 | 0% | 1.4% | #DIV/0!
G | Clothes Washer Water Efficiency (WF) | (g) | 9.5 | 6.5 |  |  |  |  | 1 | 0 | 1 |  | 0.2 | 0 | 0 | 0 | 0 | 0% | 21.7% | #DIV/0!
H | Water used to reach 100 degrees (Gallons) | (h) | 2 | 0.75 | [5 empty] | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0% | 13.7% | #DIV/0!
I | Rainwater captured for indoor water use | (i), (j) | 0 | 0 |  |  |  |  | 1 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0% |  | #DIV/0!
Totals | [13 empty] | 0 | 0 | 0 | 0 | Projected Gallons Saved per Day
The WEiR (Water Efficiency indoor Rating) Index can range from 0 to greater than 100 with a lower index number being better. | [16 empty] | WEiR index for this project is |  |  |  |  | but is NOT YET CONFIRMED.
| Indoor Gallons Saved per Day |  |  |  | 0 | [11 empty] | Annual Indoor Gallons Saved |  |  |  |  | 0
Notes
(a) | GPF = Gallons/Flush; GPM = Gallons/Minute
(b) | If more than one toilet is installed in the home, average the GPF of all the toilets for the WEiR index.
(c) | If more than one showerhead is installed in the home, average the GPM of all the showerheads for the WEiR index.
(d) | If more than one lavatory faucet is installed in the home, average the GPM of all the lavatory faucets for the WEiR index.
(e) | If more than one kitchen faucet is installed in the home, count only the faucet that serves the sink next to the dishwasher.
(f) | If more than one dishwasher is installed in the home, average the gallons per cycle (GPC) of all the dishwashers for the WEiR index. A source for determining GPC of dishwashers is http://www.energystar.gov/productfinder/product/certified-residential-dishwashers/.
(g) | Water factor (WF) is the quotient of the total weighted per-cycle water consumption divided by the capacity of the clothes washer. More water-efficient clothes washers have lower water factors. A source for determining the WF of clothes washers is http://www.appliances.energy.ca.gov/QuickSearch1024.aspx.
(h) | To determine the water used (wasted) to reach 100 degrees the verifier must do the following:
| (1) | For non-circulation systems (all types) - Determine the water fixture to be tested. This fixture shall be the showerhead or kitchen faucet (closest to the dishwasher if more than one) that is farthest from the hot water source (hot water heater or storage tank). Run no hot water through the system for 1 hour. Perform the measurement as follows. Run hot water only (no cold water) from the fixture to be tested into a measurement container. Using a fast-reading digital thermometer, stop the flow when the temperature from the fixture reaches 100 degrees. Record the amount of water wasted before reaching 100 degrees in the WEiR table above.
| 2) | For all circulation systems - Fixtures to be tested include all showerheads (including each showerhead in enclosures with multiple showerheads) and the kitchen faucet closest to the dishwasher. Initiate the circulation system for 2 minutes before starting the test. Perform the test on each fixture as follows. Run hot water only (no cold water) from the fixture to be tested into a measurement container. Using a fast-reading digital thermometer, stop the flow when the temperature from the fixture reaches 100 degrees. Note the amount of water wasted before 100 degrees. Repeat for all required fixtures. Record the worst-case amount of water wasted before reaching 100 degrees in the WEiR table above.
(i) | Rainwater capture (or other legal water capture and reuse such as greywater, etc.) for reuse indoors: Chart for calculations is under development.
(j) | Water savings can not exceed water use of fixtures supplied with rainwater (or other legal reused water). Fixtures must be piped with 'purple pipe'.
(k) | Bathtub input is not used for the WEiR index calculation but is used for greywater reuse calculations if a greywater system is installed.
Note on L20: Steve Vollstedt: Per Steve Hale, change to 'bedrooms' from 'bedrooms + 1'.

## 4b Indoor Water Testing
[9 empty] | Version 2015.05 (Dec 2015) |  | WEiR Index Verification & Testing of Indoor Water Fixtures & Appliances
H O M E A D D R E S S A N D V E R I F I E R I N F O R M A T I O N
Project Address: | [6 empty] | Name of Verifier:
Verifier's Company Name:
Verifier's Email Address:
Builder: | [6 empty] | Date(s) of Testing & Verification:
Dishwashers
Verify must determine GPC of water used for dishwashers. A source for this information is www.energystar.gov/productfinder/product/certified-residential-dishwashers/.
Number of Dishwashers | Location | GPC per Manufacturer Specification | Manufacturer and Model Number of Dishwasher |  |  | Notes
0 | Average GPC --> |  | <-- ENTER ON WEiR TAB.
Kitchen Faucets
Kitchen faucet flow rates per manufacturer must be determined for each different faucet model installed. If verifier cannot determine flow rate per manufacturer, verifier should measure the flow rate and enter the GPM flow rate rounded Up to the next 0.5 gallon. Verifier must test GPM flow rate of each different faucet model installed in each home. For production builders, verification of flow rates for a model of faucet may be discontinued after verifier has tested flow rates of 5 faucets of that model. Water wasted before reaching 100° must be measured by verifier for kitchen faucet nearest to the dishwasher as follows. If the home has a hot water recirculation loop, the amount of water discharged from the faucet before the temperature rises to 100° must be measured. If the home does not have a hot water recirculation loop, the amount of water discharged from the faucet nearest to the dishwasher before the temperature rises to 100° must be measured.
Number of Faucets | Location | GPM per Manufacturer Specification | Manufacturer and Model Number of Faucet (or how GPM determined) |  |  | Tested GPM Flow Rate (test each model installed) |  | Measured Volume of Weater Wasted Before 100° Temperature
[8 empty] | Ounces before 100° | Gallons before 100° | Explanation of How Ounces of Water Wasted Before Temperature Reaches 100° Was Measured
| Kitchen faucet closest to dishwasher | [7 empty] | 0
0 | Average GPM --> |  | <-- ENTER ON WEiR TAB.
Clothes Washers
Verifier must determine Intergated Water Factor for clothes washers to determine WEiR. A source for the IWF is www.energystar.gov/productfinder/product/certified-clothes-washers/. Verifier can also collect the following specifications required for the HERS rating: Modified Energy Factor (MEF) or Integrated Modified Energy Factor (IMEF), Label Energy Rating (LER) which is the estimated kWh/y, and the washer capacity in cubic feet.
Manufacturer, Brand and Model Number |  |  |  |  | Integrated Water Factor (IWF) | MEF or IMEF | LER (kWh/y) | Capacity (cu. ft.) | Notes
Maximum Integrated Water Factor (IWF) --> |  |  |  |  | 0 | <-- ENTER ON WEiR TAB.
Showerheads
Showerhead flow rates per manufacturer must be determined for each different showerhead model installed. If verifier cannot determine flow rate per manufacturer, verifier should measure the flow rate and enter the GPM flow rate rounded Up to the next 0.5 gallon. Verifier must test GPM flow rate of each different showerhead model installed in each home. For production builders, verification of flow rates for a model of showerhead may be discontinued after verifier has tested flow rates of 5 showerheads of that model. Water wasted before reaching 100° must be measured by verifier as follows. If the home has a hot water recirculation loop, the amount of water discharged from every showerhead before the temperature rises to 100° must be measured. If the home does not have a hot water recirculation loop, the amount of water discharged from the showerhead furthest from the hot water source before the temperature rises to 100° must be measured.
Number of Showerheads | Location | GPM per Manufacturer Specification | Manufacturer and Model Number of Showerhead (or how GPM determined) |  |  | Tested GPM Flow Rate (test each model installed) |  | Measured Volume of Weater Wasted Before 100° Temperature
[8 empty] | Ounces before 100° | Gallons before 100° | Explanation of How Ounces of Water Wasted Before Temperature Reaches 100° Was Measured
0
0
0
0
0
0 | Average GPM per Manufacturer --> |  | <-- ENTER ON WEiR TAB.
Lavatory Faucets
Lavatory faucet flow rates per manufacturer must be determined for each different faucet model installed. If verifier cannot determine flow rate per manufacturer, verifier should measure the flow rate and enter the GPM flow rate rounded Up to the next 0.5 gallon. Verifier must test GPM flow rate of each different faucet model installed in each home. For production builders, verification of flow rates for a model of faucets may be discontinued after verifier has tested flow rates of 5 faucets of that model.
Number of Faucets | Location | GPM per Manufacturer Specification | Manufacturer and Model Number of Lavatory Faucet (or how GPM determined) |  |  |  | Tested GPM Flow Rate (test each model installed) |  | Notes
z
0 | Average GPM --> |  | <-- ENTER ON WEiR TAB.
Toilets | [7 empty] | Water Wasted to Reach 100° Temperature at 'Worst Case' Fixture
Toilet flush volumes per manufacturer must be determined but no testing is required.
Number of Toilets | Location | GPF per Mfr Spec | How was GPF volume determined? - Label on toilet, manufacturer's specification sheet, WaterSense label, etc. |  |  |  |  | Gallons
[8 empty] | 0 | Worst case volume of water wasted before reaching 100°, in gallons. ENTER ON WEiR Tab.
0 | Average GPF per Manufacturer --> |  | <-- ENTER ON WEiR TAB.
Hot Water Circulation System
Verify must determine if the home has a hot water recirculation loop that services all shower areas and the kitchen. Determine if the recirculation pump is constantly on, is controlled by a timer, is controlled by a 'smart' controller, or is a 'demand controlled' system using a switches and/or motion sensors. Also determine if the system is equipped with an aquastat sensor to turn off the recirculation pump when the return water temperature is at least 100°.
Type of hot water recirculation system | [5 empty] | If recirculation system installed, is there an aquastat sensor?
Water Leakage Test
Verifier can perform a water leakage test to earn a point for practice 2.4.13. To perform the test, follow these steps: (1) attach a water pressure guage, (2) measure & record the beginning pressure, (3) turn the main water valve off, (4) wait at least 10 minutes, (5) measure & record the ending pressure, (6) turn the main water valve back on. If the beginning and ending water pressure measurements the is no water leak and the home passes the water leakage test.
Was a Water Leakage Test Performed? | Beginning Water Pressure (PSI) | Ending Water Pressure (PSI) |  | Water Leakage Test Result - Pass or Fail |  | Notes
Not Tested
Verifier Notes & Comments - Other
BGNM Documentation and Photo Requirements

## 5 HVAC Accountability Form
HVAC Accountability Form
Version 2015.05 (Dec 2015)
Project Data
Project Address:
The following HVAC practices, if applicable, must be completed and verified as having been completed by signature of the HVAC contractor for points to be awarded by BGNM for BGNM certification.
Practice # | Building Practice Summary | Was This Practice Satisfied?
1.2.1 | Equipment sizing. Space heating and space cooling systems shall be sized in accordance with ACCA Manual S based on building loads calculated in accordance with ACCA Manual J, or other approved heating and cooling equipment sizing methodologies. MANDATORY
1.2.2 | Heating and cooling distribution systems. Space heating and cooling distribution systems shall be designed and installed following the practices below, if applicable:
(a) Heating and cooling distribution systems using ducting shall be sized and designed in accordance with ACCA Manual D, or equivalent. Heating and cooling distribution systems not requiring ducting shall be designed following appropriate industry guidelines and practices. Load calculation and equipment sizing reports must be provided to Green Verifier. Heating and/or cooling distribution design reports, including duct design reports (if applicable) shall be provided to the Green Verifier. MANDATORY
(b) All forced air space heating and space cooling duct distribution systems shall be air-sealed. All duct sealing materials shall be in conformance with UL 181A or UL181B specifications and shall be installed in accordance with manufacturer's instructions. MANDATORY
(c) Building cavities shall not be used as supply or return ducts. Industry-approved duct materials shall be used to minimize leakage of conditioned air. This includes plenums such as platforms under forced air systems for return air. All such cavities shall be lined and sealed with appropriate duct materials. MANDATORY
(d) Boiler supply piping and domestic hot water supply piping located in unconditioned spaces shall be insulated to R-3, or higher. MANDATORY
(e) A return air path shall be provided for every room with a door (i.e. return ducts or transfer grills) for forced-air heating and cooling distribution systems. Return ducts or transfer grills are not required for bathrooms, kitchens, closets, pantries and laundry rooms.
(f) Balanced HVAC airflows are demonstrated by flow hood or other acceptable flow measurement tool by a third party. Test results are in accordance with both of the following requirements. A Manual D report evidencing the results of the testing is provided to the third-party verifier: (1) Measured flow at each supply and return register is within 25% of design flow, OR (2) Total airflow is within 10 percent of design flow
1.2.3 | HVAC system performance testing. Performance of the heating and cooling systems is verified by the HVAC contractor in accordance with all of the following, if applicable, and the Accountability Form for HVAC System Performance Testing is provided to the verifier:
(a) Start-up procedure is performed in accordance with the manufacturer's instructions. MANDATORY
(b) Burner is set to fire at input level listed on nameplate (combustion equipment).
(c) Refrigerant charge is verified by super-heat and/or sub-cooling method.
(d) Air handler settings and fan speed(s) are set in accordance with manufacturer's instructions.
(e) Duct leakage testing is performed by third-party verifier per RESNET protocol demonstrating that the entire air distribution system including ducts, air handlers and register boots has measured duct leakage to outside at a pressure differential of 25 Pascals of no greater than 4 cfm per 100 square feet of conditioned floor area.
1.2.4 | HVAC contractor and service technician are certified. Nationally or regionally recognized program (e.g. North American Technician Excellence, Inc. (NATE), Air Conditioning Contractors of America Quality Assured Program (ACCA/QA), Building Performance Institute (BPI), or a manufacturer's training program is acceptable.
Builder Declaration of Compliance
I declare that the practices claimed by my company, subcontractors and or suppliers meet the requirements necessary to comply with the practices claimed above.
HVAC Contractor 1
Company Name
Name of Responsible Contractor
Contact Email
Contact Phone Number
Signature of Responsible Contractor
HVAC Contractor 2
Company Name
Name of Responsible Contractor
Contact Email
Contact Phone Number
Signature of Responsible Contractor
Electronic signature allowed

## 6 Thermal Enclosure Checklist
|  | Address of Project Home: |  |  |  | Thermal Enclosure System Checklist |  |  | Verification List
OK
See Note, below
|  | Climate Zone of Project Home: | [6 empty] | Not Applicable
Version 2015.05 (Dec 2015)
Practice # | Thermal Enclosure System Practice |  |  |  |  | Builder Verified | Rater Verified | Not Applicable
BGNM's Thermal Enclosure System Checklist is similar to the ENERGY STAR Certified Homes Thermal Enclosure System Rater Checklist, Version 3. Further interpretations, definitions and guidance for BGNM's Thermal Enclosure System Checklist may be found in the Notes and guidelines provided with the ENERGY STAR Certified Homes Thermal Enclosure System Rater Checklist. For homes that are ENERGY STAR-certified, BGNM will accept the current version of the ENERGY STAR Thermal Enclosure System Rater Checklist in lieu of this BGNM Thermal Enclosure System Checklist to minimize duplicative requirements.
1. High-Performance Fenestration
1.1 | Fenestration shall meet or exceed 2009 IECC requirements
2. Quality-Installed Insulation
2.1 | Ceiling, wall, floor, and slab insulation levels (R-values or U-factors) shall meet or exceed 2009 IECC requirements
2.2 | All ceiling, wall, floor and slab insulation shall achieve RESNET-defined Grade I installation or, alternatively, Grade II for surfaces that contain a layer of continuous, air impermeable insulation with R-value of at least R-3 in Climate Zones 1 to 4, and R-5 in Climate Zones 5 to 8.
3. Fully-Aligned Air Barriers
At each insulated location below, a complete air barrier shall be provided that is fully aligned with the insulation as follows: * At interior or exterior surfaces of ceilings in Climate Zones 1-3; at interior surfaces of ceilings in Climate Zones 4-8. Also, include barrier at interior edge of attic eave in all climate zones using a wind baffle that extends to the full height of the insulation. Include a baffle in every bay or a tabbed baffle in each bay with a soffit vent that will also prevent wind washing of insulation in adjacent bays * At exterior surface of walls in all climate zones; and also at interior surface of walls for Climate Zones 4-8 * At interior surfaces of floors in all climate zones, including supports to ensure permanent contact and blocking at exposed edges
3.1 | Walls
3.1.1 | Walls behind showers and tubs
3.1.2 | Walls behind fireplaces
3.1.3 | Attic knee walls
3.1.4 | Skylight shaft walls
3.1.5 | Walls adjoining porch roofs
3.1.6 | Staircase walls
3.1.7 | Double walls
3.1.8 | Garage rim/band joists adjoining conditioned space
3.1.9 | All other exterior walls
3.2 | Floors
3.2.1 | Floors above garage
3.2.2 | Cantilevered floors
3.2.3 | Floors above unconditioned basements or unconditioned crawlspaces
3.3 | Ceilings
3.3.1 | Dropped ceilings/soffits below unconditioned attics
3.3.2 | All other ceilings
4. Reduced Thermal Bridging
4.1 | For insulated ceilings with attic space above (i.e. non-cathedral), Grade I installation extends to the inside face of the exterior wall below at theses levels: CZ 1-5: at least R-21; CZ 6-8: at least R-30
4.2 | For slabs on grade in CZ 4 and higher, 100% of slab edge insulated to at least R-5 at the depth specified by the 2009 IECC and aligned with thermal boundary of the walls
4.3 | Insulation beneath attic platforms (e.g., HVAC platforms, walkways) at least R-21 in CZ 1-5; at least R-30 in CZ 6-8
4.4 | Reduced thermal bridging at above-grade walls separating conditioned from unconditioned spaces (rim/band joists exempted) using one or more of the following options:
4.4.1 | Continuous rigid insulation, insulated siding, or combination of the two; at least R-3 in CZ 1-4, at least R-5 in CZ 5-8, OR;
4.4.2 | Structural insulated panels (SIPs), OR;
4.4.3 | Insulated concrete forms (ICFs), OR;
4.4.4 | Double-wall framing, OR;
4.4.5 | Advanced framing including all of the items below:
4.4.5.1 | All corners insulated to at least R-6, AND;
4.4.5.2 | All headers above windows and doors insulated to at least R-3 for 2x4 framing or equivalent cavity width, and at least R-5 for all other assemblies (e.g., with 2x6 framing), AND;
4.4.5.3 | Framing limited at all windows and doors to one pair of king studs, plus one pair of jack studs per window opening to support the header and sill, AND;
4.4.5.4 | All interior/exterior wall intersections insulated to the same R-value as the rest of the exterior wall, AND;
4.4.5.5 | Stud spacing of 16 in. o.c. for 2x4 framing in all Climate Zones and, in CZs 5-8, 24 in. o.c. for 2x6 framing
5. Air Sealing
5.1 | Penetrations to unconditioned spaces fully sealed with solid blocking or flashing as needed and gaps sealed with caulk or foam
5.1.1 | Duct and flue shafts
5.1.2 | Plumbing and piping
5.1.3 | Electrical wiring
5.1.4 | Exhaust fans
5.1.5 | Recessed lighting fixtures adjacent to unconditioned spaces are insulation-contact, air-tight (ICAT) labeled and fully gasketed. Also, if in insulated ceiling with attic space above, exterior surface of fixture insulated to at least R-10 in CZ 4 and higher to minimize condensation potential.
5.1.6 | Light tubes adjacent to unconditioned spaces include lenses separating unconditioned and conditioned spaces and are fully gasketed.
5.2 | Cracks in the building enclosure fully sealed
5.2.1 | All above-grade sill plates adjacent to conditioned spaces sealed to foundations or sub-floors with caulk, foam, or equivalent material. Foam gasket also placed beneath above-grade sill plate if resting atop concrete or masonry and adjacent to conditioned space
5.2.2 | At tops of walls adjoining unconditioned spaces, continuous top plates or sealed blocking using caulk, foam, or equivalent material
5.2.3 | FOR BGNM CERTIFICATIONS THIS PRACTICE IS NOT REQUIRED BUT BGNM ENCOURAGES IMPLEMENTING THIS PRACTICE. Drywall sealed to top plates at all unconditioned attic to wall interfaces using caulk, foam, drywall adhesive (but not other construction adhesives), or equivalent material. Either apply sealant directly between drywall and top plate or to the seam between the two from the attic above.
5.2.4 | Rough openings around windows and exterior doors sealed with caulk or foam
5.2.5 | Marriage joints between modular home modules at all exterior boundary conditions fully sealed with gasket & foam
5.2.6 | All seams between Structural Insulated Panels (SIPs) foamed and/or taped per manufacturer's instructions
5.2.7 | In multifamily buildings, the gap between the common wall (e.g. the drywall shaft wall) and the structural framing between units fully sealed at all exterior boundaries
5.3 | Other openings
5.3.1 | Doors adjacent to unconditioned spaces (e.g. attics, garages, basements) or ambient conditions made substantially air-tight with weather-stripping or equivalent gasket
5.3.2 | Attic access panels and dropdown stairs equipped with a durable insulated cover of at least R-10 that is gasketed (not caulked) to produce continuous air seal when occupant is not accessing the attic
5.3.3 | Whole-house fans equipped with a durable insulated cover of at least R-10 that is gasketed and either installed on the house side or mechanically operated
VERIFIER & BUILDER NOTES (Reference back to Practice # above)
REQUIRED SIGNATURES FOR VERIFICATIONS AND INSPECTIONS
Rater Company Name |  |  | Rater Name |  | Rater Signature
Builder Company Name |  |  | Builder Representative Name |  | Builder Representative Signature
Date(s) of Rough Inspection(s): |  |  |  | Date(s) of Final Inspection(s)
END OF THERMAL ENCLOSURE SYSTEM CHECKLIST

## 7 NM Climate Zones
New Mexico Climate Zones
City | County | Elevation (feet) | Heating Degree Days (HDD, 65° F) |  | Cooling Degree Days (CDD, XX°F) | Climate Zone
The information in the table below is from Table 301.2 in Section 14.7.6.11 of the New Mexico Administrative Code. Locations not listed in the table below shall use either Table 301.1, Section 301.3, or the building official may designate a climate zone consistent with the elevation, HDD and CDD from the table below for the unlisted location. BGNM encourages users to refer back to the NM Administrative Code to determine if any changes have been made since the information below was obtained.
Abiquiu Dam | Rio Arriba | 6380 | 5872 |  |  | 5-B
Angel Fire | Colfax | 8406 | 9769 |  | 195 | 7-B
Alamagordo | Otero | 4350 | 3053 |  | 5309 | 3-B
Albuquerque | Bernalillo | 5312 | 4332 |  | 4462 | 4-B
Artesia | Eddy | 3380 | 3366 |  | 5374 | 3-B
Aztec Ruins | San Juan | 5644 | 5757 |  |  | 5-B
Belen | Valencia | 4800 | 4432 |  | 5012 | 3-B
Bernalillo | Sandoval | 5052 | 4782 |  | 4138 | 4-B
Bloomfield | San Juan | 5456 | 5490 |  |  | 5-B
Bosque del Apache | Socorro | 4520 | 3916 |  | 5012 | 3-B
Carlsbad | Eddy | 3295 | 2813 |  | 5997 | 3-B
Carrizozo | Lincoln | 5438 | 4234 |  | 3631 | 4-B
Cedar Crest | Bernalillo | 6581 | 5703 |  |  | 5-B
Chaco Canyon | San Juan | 6200 | 6137 |  |  | 5-B
Chama | Rio Arriba | 7871 | 8254 |  |  | 6-B
Clayton | Union | 5056 | 5150 |  | 3170 | 4-B
Cloudcroft | Otero | 8801 | 7205 |  |  | 6-B
Clovis | Curry | 4268 | 4033 |  | 4252 | 4-B
Corona | Valencia | 6690 | 5389 |  | 3631 | 4-B
Cuba | Sandoval | 7035 | 7122 |  |  | 5-B
Deming | Luna | 4305 | 3347 |  | 5292 | 3-B
Dulce | Rio Arriba | 6793 | 7979 |  |  | 6-B
Eagle Nest | Colfax | 8262 | 9254 |  |  | 7-B
Edgewood | Santa Fe | 6649 | 6146 |  |  | 5-B
Espanola | Rio Arriba | 5643 | 5641 |  |  | 5-B
Farmington | San Juan | 5395 | 5747 |  |  | 5-B
Fence Lake | Cibola | 7055 | 6396 |  |  | 5-B
Fort Sumner | De Baca | 4032 | 3799 |  | 4616 | 3-B
Gallup | McKinley | 6465 | 6207 |  |  | 5-B
Glenwood | Catron | 4725 | 3632 |  | 4427 | 4-B
Grants | Cibola | 6460 | 6143 |  |  | 5-B
Hatch | Dona Ana | 4052 | 3270 |  | 5904 | 3-B
Hobbs | Lea | 3622 | 2954 |  | 5181 | 3-B
Jemez Springs | Sandoval | 6198 | 5260 |  | 2059 | 4-B
Las Cruces | Dona Ana | 4000 | 3223 |  | 5904 | 3-B
Las Vegas | San Miguel | 6424 | 5738 |  |  | 5-B
Lordsburg | Hidalgo | 4250 | 3213 |  | 5210 | 3-B
Los Alamos | Los Alamos | 7320 | 6381 |  |  | 5-B
Los Lunas | Valencia | 4856 | 4725 |  | 4462 | 4-B
Magdalena | Socorro | 6572 | 5074 |  | 2093 | 4-B
Mescalero | Otero | 6611 | 5540 |  |  | 5-B
Moriarty | Torrance | 6220 | 4735 |  | 3786 | 4-B
Mosquero | Harding | 5485 | 5209 |  | 3631 | 4-B
Mountainair | Torrance | 6520 | 5558 |  |  | 5-B
Organ | Dona Ana | 5245 | 3215 |  | 4919 | 3-B
Placitas | Sandoval | 5955 | 4917 |  | 3701 | 4-B
Portales | Roosevelt | 4006 | 3845 |  | 4347 | 4-B
Raton | Colfax | 6680 | 6001 |  |  | 5-B
Red River | Taos | 8671 | 8742 |  | 179 | 7-B
Reserve | Catron | 5847 | 5483 |  |  | 5-B
Rio Rancho | Sandoval | 5282 | 4880 |  | 3949 | 4-B
Roswell | Chaves | 3573 | 3565 |  | 5505 | 3-B
Ruidoso | Lincoln | 6920 | 6309 |  |  | 5-B
Sandia Crest | Bernalillo | 10680 | 10034 |  |  | 7-B
Sandia Park | Bernalillo | 7077 | 7510 |  |  | 6-B
Santa Fe | Santa Fe | 7260 | 6001 |  |  | 5-B
Santa Rosa | Guadalupe | 4620 | 3749 |  | 4714 | 3-B
Shiprock | San Juan | 4892 | 5475 |  |  | 5-B
Silver City | Grant | 5895 | 4438 |  | 3975 | 4-B
Socorro | Socorro | 4603 | 3984 |  | 5147 | 3-B
Springer | Colfax | 5797 | 5653 |  |  | 5-B
Taos | Taos | 6967 | 6827 |  |  | 5-B
Taos Ski Valley | Taos | 9321 | 9769 |  |  | 7-B
Tatum | Lea | 3999 | 3680 |  | 4721 | 3-B
Thoreau | McKinley | 7200 | 5789 |  |  | 5-B
Tierra Amarilla | Rio Arriba | 7425 | 7901 |  |  | 6-B
Tijeras | Bernalillo | 6322 | 6338 |  |  | 5-B
Tohatchi | McKinley | 6447 | 5418 |  |  | 5-B
Truth or Consequences | Sierra | 4245 | 3394 |  | 5103 | 3-B
Tucumcari | Quay | 4096 | 3767 |  | 4429 | 4-B
Tularosa | Otero | 4508 | 3056 |  | 5130 | 3-B
Zuni | McKinley | 6293 | 5742 |  |  | 5-B

## 8 IECC Insulation Requirements
IECC Insulation Requirements
2009 IECC -- Table 402.1.1 Insulation and Fenestration Requirements by Component (a) The insulation requirements below is from the 2009 International Energy Conservation Code (IECC). This information is reproduced below for your convenience. You should refer to the 2009 IECC for the footnote references and to the general IECC requirements for the building thermal envelope.
Climate Zone | Fenestration U-Factor (b) | Skylight U-Factor (b) | Glazed Fenestration SHGC (b) (e) | Ceiling R-Value | Wood Frame Wall R-Value | Mass Wall R-Value (i) | Floor R-Value | Basement Wall R-Value (c) | Slab R-Value & Depth (d) | Crawl Space Wall R-Value (c)
3 | 0.50 (j) | 0.65 | 0.3 | 30 | 13 | 5/8 | 19 | 5/13 (f) | 0 | 5/13
4 | 0.35 | 0.6 | No Requirement | 38 | 13 | 5/10 | 19 | 10/13 | 10, 2 ft. | 10/13
5 | 0.35 | 0.6 | No Requirement | 38 | 20 or 13+5 (h) | 13/17 | 30 (g) | 10/13 | 10, 2 ft. | 10/13
6 | 0.35 | 0.6 | No Requirement | 49 | 20 or 13+5 (h) | 15/19 | 30 (g) | 15/19 | 10, 4 ft. | 10/13
7 | 0.35 | 0.6 | No Requirement | 49 | 21 | 19/21 | 30 (g) | 15/19 | 10, 4 ft. | 10/13
2015 IECC -- Table 402.1.1 Insulation and Fenestration Requirements by Component (a) The insulation requirements below is from the 2015 International Energy Conservation Code (IECC). This information is reproduced below for your convenience. You should refer to the 2015 IECC for the footnote references and to the general IECC requirements for the building thermal envelope.
Climate Zone | Fenestration U-Factor (b) | Skylight U-Factor (b) | Glazed Fenestration SHGC (b) (e) | Ceiling R-Value | Wood Frame Wall R-Value | Mass Wall R-Value (i) | Floor R-Value | Basement Wall R-Value (c) | Slab R-Value & Depth (d) | Crawl Space Wall R-Value (c)
3 | 0.35 | 0.55 | 0.25 | 38 | 20 or 13+5 (h) | 8/13 | 19 | 5/13 (f) | 0 | 5/13
4 | 0.35 | 0.55 | 0.4 | 49 | 20 or 13+5 (h) | 8/13 | 19 | 10/13 | 10, 2 ft. | 10/13
5 | 0.32 | 0.55 | No Requirement | 49 | 20 or 13+5 (h) | 13/17 | 30 (g) | 15/19 | 10, 2 ft. | 15/19
6 | 0.32 | 0.55 | No Requirement | 49 | 20+5 or 13+10 (h) | 15/20 | 30 (g) | 15/19 | 10, 4 ft. | 15/19
7 | 0.32 | 0.55 | No Requirement | 49 | 20+5 or 13+10 (h) | 19/21 | 38 (g) | 15/19 | 10, 4 ft. | 15/19

## Errata
Errata of Version Changes
Version 2015.05 (Dec 2015)
Date | Version | Correction or Change
2015-02-05 | 2015.01 | Initial release of the BGNM certification program using BGNM's own version of the scoring tool instead of the 2012 NGBS.
2015-03-05 | 2015.02 | Corrected 'Water used to reach 100 degrees' calculations on '4 WERS Index' tab.
2015-03-05 | 2015.02 | Added fillable thermal bypass checklist -- '6 Thermal Bypass'.
2015-04-29 | 2015.02 | Reformatted text cells to 'general' from 'text' throughout workbook so cell contents will display properly without '######'.
2015-05-16 | 2015.03 | Verification & Testing section added at bottom of tab '4 WEiR Index' to capture information related to verification & testing of water fixtures & appliances. Added project information at top of sheet and linked some cells to verification & testing section.
2015-05-17 | 2015.03 | Replaced '5 Accountability Form' tab with '5 HVAC Accountability Form'. Other items previously on the accountability form were dealt with by requiring notes on the '3 Scoring & Verification' tab.
2015-05-17 | 2015.03 | Updated '2 Project Information' tab to say certification submission needs HERC without PV and 2015 IECC UA compliance report needed if points are taken. |  | z
2015-06-15 | 2015.03 | Corrected points allowed for practice 3.7.6 on '3 Scoring & Verification' tab to indicate that 0.5 points allowed per category, up to 1.0 points.
2015-06-15 | 2015.03 | Revised practice 2.4.8 on tab '3 Scoring & Verification' tab to allow up to 1.0 points for automatic shower flow restriction valve when water temperature reaches =>95°.
2015-06-15 | 2015.03 | Added logic on '4 WEiR Index' tab to not display message about entering number of bedrooms if the number of bedrooms was entered on '2 Project Information' tab.
2015-06-23 | 2015.03 | Corrected scoring logic at row 211 on '3 Scoring & Verification' tab.
2014-06-24 | 2015.03 | Corrected certification fee on '2 Project Information' tab from $200 to $245.
2015-06-29 | 2015.03 | Added information block at bottom of '3 Scoring & Verification' tab to identify third-party verifier and for signature.
2015-07-14 | 2015.03 | Modified '4a WEiR Index' tab to remove bathtub water use from WEiR index calculation (per Steve Hale)
2015-07-17 | 2015.03 | Edited '1 BGNM Program Overview' tab to better explain some program changes.
2015-07-17 | 2015.03 | Modified formula on '4a WEiR Index' tab to remove lavatory faucets in calculations related to water wasted before 100 degrees.
2015-07-18 | 2015.03 | On '3 Scoring & Verification' tab changed points for practice 2.1.2.
2015-07-20 | 2015.03 | On '3 Scoring & Verification' tab changed wording for epaporative cooling systems to read water flushes to reduce minerals and salts.
2015-07-20 | 2015.03 | On '4a WEiR Index' tab made numerous changes to Notes. Most significant changes were testing procedures for water wasted to reach 100 degrees.
2015-07-20 | 2015.03 | On '4b Indoor Water Testing' tab made several changes to conform this sheet to WEiR index requirements.
2015-07-21 | 2015.03 | On '3 Scoring & Verification' tab increased points available for practice 2.2.2(b).
2015-07-21 | 2015.03 | On '4a WEiR Index' tab corrected notes for testing water wasted before reaching 100 degrees.
2015-07-23 | 2015.03 | On '4b Indoor Water Testing' tab made change to deal with water wasted before 100 degrees when there is not a recirculation system.
2015-08-28 | 2015.04 | On '4b Indoor Water Testing' tab made change to deal with water gpm when quantity greater than 1 is enterred on a line.
2015-11-07 | 2015.04 | Workbook received back from SO with changes per approval from SH.
2015-11-18 | 2015.05 | Modified '4b Indoor Water Testing' tab to provide more clear directions and to be more intuitive.

## Indoor_Values (HIDE) (hidden)
Indoor Values
EPA 1992 | Baseline Fixtures, per EPAct 1992 |  | Fixture Use
(INDUSTRY) | Fixture | Flow Rate | Duration (sec) | Uses/Day/Occupant | Gallons/Use
| Baseline Toilets (GPF) | 1.6 | - | 5
| Baseline Urinals (GPF) | 1 | - | 5
| Baseline Showerheads (GPM) | 2.5 | 300 | 1
| Tub Faucet (GPM) | 3 |  |  | 10 | Steve Vollstedt entered 10 gallons per use to use for grey water calculations
| Baseline Bathroom Faucets (GPM) | 2.2 | 15 | 5
| Baseline Kitchen Faucets (GPM) | 2.2 | 60 | 1 |  | Steve Hale requested kitchen faucet use per day for each occupant for hot water draws be changed to 1 from 4.
| Dishwasher (GPC) | 6.5
| Washing Machine Water Factor (WF) - Water consumption per load divided by clothes washer capacity in cubic feet | 9.5 |  |  |  | PREVIOUS WORDING OF CELL B11 -- Washing Machine (WF) water factor / water efficiency
| Clothes Washer Gallons per Load per H2ouse.org | 40.9 |  |  |  | STEVE VOLLSTEDT ADDED THIS ROW
| Water used to reach 100 degrees (Gallons) | 2
Hot water recirculation loop
| USES PER DAY PER OCCUPANT (GENERAL) |  |  | 4
STEVE HALE NOTES:
BGNM | Baseline Fixtures, per BGNM |  | Fixture Use |  |  | NEED BASE LINE INDUSTRY STANDARD COLUMN FOR "100"
| Fixture | Flow Rate | Duration (sec) | Uses/Day/Occupant |  | NEED ANOTHER COLUMN TO SHOW BUILDING PROGRAM REQUIREMENTS (BGNM IS ENERGY STAR & WATER SENSE)
| Baseline Toilets (GPF) | 1.28
| Baseline Urinals (GPF) | 1
| Baseline Showerheads (GPM) | 2
| Tub Faucet (GPM) | 3
| Baseline Bathroom Faucets (GPM) | 1.5
| Baseline Kitchen Faucets (GPM) | 2.2
| Dishwasher (GPC) | 4.25 |  | 1
| Washing Machine Water Factor (WF) - Water consumption per load divided by clothes washer capacity in cubic feet | 6 |  | 0.2 |  | PREVIOUS WORDING OF CELL B25 -- Washing Machine (WF) water factor / water efficiency Uses per Day per Occupant = 0.2 per Steve Hale.
| Water used to reach 100 degrees (Gallons) | 0.75
Hot water recirculation loop
Other
AWWA | PERCENT USE per AWWA |  |  |  |  | http://www.home-water-works.org/indoor-use
| Fixture | Percent of Overall use
| Baseline Toilets | 26.7% |  |  |  | http://www.home-water-works.org/indoor-use/toilets
Baseline Urinals
| Baseline Showerheads | 16.8% |  |  |  | http://www.home-water-works.org/indoor-use/showers
| Bath | 1.8%
| Baseline Lavatory Faucets | 7.7% |  |  |  | http://www.home-water-works.org/indoor-use/faucet
| Baseline Kitchen Faucets | 8%
| Dishwasher | 1.4% |  |  |  | http://www.home-water-works.org/indoor-use/dishwasher
| Clothes Washer | 21.7% |  |  |  | http://www.home-water-works.org/indoor-use/clothes-washer
| Leak | 13.7% |  |  |  | http://www.home-water-works.org/indoor-use/leaks
| Other | 2.2%
100%
Note on C39: Steve Vollstedt: Use 8% per Jan 27, 2015 phone conversation with Steve Hale.

## Lists (HIDE) (hidden)
PointList1 | PointList2 | PointList3 | PointList4 | PointList5 | PointList6 | PointList7
Not Met | Not Met
Will Be Done | Not Applicable | 0 | 0 | 0 | 0 | 0
M36, M38 | Will Be Done | 0.5 | 1 | 2 | 1 | 3
| M39, M40, M41 |  |  |  | 2
PointList8 | PointList9 | PointList10 | PointList11 | PointList12 | PointList13 | PointList14
Not Met | Not Met
Verified by Verifier | Accountability Form Verified | Not Applicable | 0 | 0 | 0 | 0
N36 | N38 | Accountability Form Verified | 4 | 0.5 | 0.5 | 0.5
|  |  |  | 1 | 1 | 1
|  |  |  | 1.5 | 1.5 | 1.5
|  |  |  | 2 | 2 | 2
|  |  |  | 2.5 |  | 2.5
|  |  |  | 3 |  | 3
|  |  |  | 3.5 |  | 3.5
|  |  |  | 4 |  | 4
|  |  |  | 4.5 |  | 4.5
5
PointList15 | PointList16 | PointList17 | PointList18 | PointList19 | PointList20 | PointList21
Not Met
Verified by Verifier | 0.5 - Builder-Certified | 1 | Will Obtain | Verifier Will Provide | 0 | Not Applicable
Not Applicable |  | 2 |  |  | 0.5 | Accountability Form Verified
|  | 3 |  |  | 1 | N39
4
PointList22 | PointList23 | PointList24 | PointList25 | PointList26 | PointList27 | PointList28
Not Met | Not Met | Not Met | Not Met | Not Met
Not Applicable | Accountability Form Verified | 0 | 1 | Not Applicable | 0 | 0
Accountability Form Verified | Verified by Verifier | 1 |  | Verified by Verifier | 2 | 1
Verified by Verifier |  |  |  |  | Not Applicable | 2
N40, N41 | [5 empty] | 3
4
5
PointList29 | PointList30 | PointList31 | PointList32 | PointList33 | PointList34
0 | 0 | 0 | 0 | None | Yes
1 | 0.5 | 1 | 1.5 | Constantly On | No
-1 | 1 | -1 | 3 | Controlled by Timer | Not Applicable
| 1.5 | -2 |  | Controlled by "Smart' Controller | Not Known
Demand-Controlled
YesNoOrNA | YesOrNo | ClimateZones | MailCertTo
Builder
Yes | Yes | 3 | Homeowner
No | No | 4 | Other
Not Applicable |  | 5
6
7